Vandeveer Plating LLC - pretreatment system operator log, August 2026

Kept by Luis Baranski, wastewater treatment operator. The Outfall 001 totalizer register is read at 07:00 each morning. The reading on a line is the register at 07:00 the following morning, so a day's flow is that reading less the one before it. Register at 07:00 on 08/01/2026: 402,867 gallons. In-line pH is the low and the high from the effluent meter chart for the day; grab pH at sampling with the Hach meter, calibrated at 06:15 on sampling days.

| Date | Totalizer at 07:00 next day, gal | In-line pH, low to high; grab at sampling | Notes |
| --- | --- | --- | --- |
| 08/01/2026 Sat | 405,823 |  | Weekend, no production; sump flow only. |
| 08/02/2026 Sun | 408,837 |  | Weekend, no production; sump flow only. |
| 08/03/2026 Mon | 446,931 | 7.5 to 7.9 | Normal operation. Chrome line running two shifts. |
| 08/04/2026 Tue | 475,421 | 7.2 to 7.8 | Normal operation. Caustic delivery, 2,100 gallons to the day tank, bill of lading in the binder. |
| 08/05/2026 Wed | 515,786 | 7.3 to 8.0 | Normal operation. Clarifier rake checked on the noon round. |
| 08/06/2026 Thu | 543,050 | 7.0 to 7.4 | Normal operation. Sampler tubing replaced ahead of the next event. |
| 08/07/2026 Fri | 571,652 | 7.2 to 7.9 | Normal operation. Polymer drum changed on the clarifier feed. |
| 08/08/2026 Sat | 575,017 |  | Weekend, no production; sump flow only. |
| 08/09/2026 Sun | 576,705 |  | Weekend, no production; sump flow only. |
| 08/10/2026 Mon | 617,789 | 7.2 to 7.9 | Normal operation. Composite sampler programmed for the 08/11 event. |
| 08/11/2026 Tue | 657,599 | 6.7 to 8.1; grab 6.8 | Routine sampling event VP-260811, grab pH 6.8 at 06:45. 24 aliquots in the bottle. |
| 08/12/2026 Wed | 686,236 | 6.9 to 7.5 | Normal operation. Sludge hauled by Kent County Disposal, 3.8 tons on the manifest. |
| 08/13/2026 Thu | 732,386 | 6.9 to 7.4 | Normal operation. Zinc line on two shifts with overtime. |
| 08/14/2026 Fri | 770,652 | 6.9 to 7.4 | Normal operation. Effluent meter chart roll changed. |
| 08/15/2026 Sat | 773,235 |  | Weekend, no production; sump flow only. |
| 08/16/2026 Sun | 775,779 |  | Weekend, no production; sump flow only. |
| 08/17/2026 Mon | 815,883 | 7.4 to 8.1 | Normal operation. Sludge press run. |
| 08/18/2026 Tue | 846,590 | 7.3 to 7.7 | Normal operation. Hach meter calibrated at 06:15 with the pH 7 and pH 10 buffers; slope within range. Composite sampler started at 06:40 for an extra Outfall 001 composite on Gordon's instruction, for the copper work, and chain of custody VP-260818 was opened for it. City crew set their sampler at manhole 44-118 at 08:15. |
| 08/19/2026 Wed | 880,719 | 7.4 to 7.8; grab 7.4 | Extra composite VP-260818 pulled at Outfall 001 at 06:40, 25 aliquots, grab pH 7.4, with a cyanide grab. Grab VP-260819 taken at the clarifier weir at 07:10, ahead of final pH adjustment, pH 9.4. City crew pulled their composite at 08:20. Ferric day tank refilled. |
| 08/20/2026 Thu | 914,241 | 7.3 to 9.2 | Normal operation. Caustic feed valve serviced at 11:00. |
| 08/21/2026 Fri | 947,766 | 7.2 to 7.7 | Normal operation. Chrome reduction ORP probe cleaned. |
| 08/22/2026 Sat | 951,034 |  | Weekend, no production; sump flow only. |
| 08/23/2026 Sun | 954,056 |  | Weekend, no production; sump flow only. |
| 08/24/2026 Mon | 994,354 | 6.8 to 7.2 | Normal operation. Composite sampler programmed for the 08/25 event. |
| 08/25/2026 Tue | 1,030,494 | 7.4 to 7.9; grab 7.5 | Routine sampling event VP-260825, grab pH 7.5 at 06:50. Low flow overnight, 19 aliquots in the bottle across the 24 hours. |
| 08/26/2026 Wed | 1,064,357 | 7.2 to 7.8 | Normal operation. Weekly walk-down of the trench and the sump with maintenance; float on RT-4 tested and passed. Lab report on the extra composite came in late in the day, copper 3.45 mg/L. |
| 08/27/2026 Thu | 1,099,817 | 7.1 to 7.6 | Normal operation. Polymer drum changed. Lab report on VP-260811 came in, copper 4.33 mg/L. Gordon told of both copper results. Left a voicemail for Renee Castellanos at 17:05 on the 3.45 copper from the extra composite. |
| 08/28/2026 Fri | 1,133,887 | 6.9 to 7.7 | Normal operation. Sludge press cloths washed. Gordon called the City at 16:10 on the 08/11 copper. |
| 08/29/2026 Sat | 1,136,948 |  | Weekend, no production; sump flow only. |
| 08/30/2026 Sun | 1,139,175 |  | Weekend, no production; sump flow only. |
| 08/31/2026 Mon | 1,173,773 | 7.0 to 7.4 | Normal operation. Month's charts pulled and filed in the binder. |

Operator's end-of-month note. Nothing went around the clarifier this month. The caustic feed valve was serviced on the 20th, and the chart for the day is in the binder with the rest of the month.