Vandeveer Plating LLC - pretreatment system operator log, July 2026

Kept by Luis Baranski, wastewater treatment operator. The Outfall 001 totalizer register is read at 07:00 each morning. The reading on a line is the register at 07:00 the following morning, so a day's flow is that reading less the one before it. Register at 07:00 on 07/01/2026: 4,850,733 gallons. In-line pH is the low and the high from the effluent meter chart for the day; grab pH at sampling with the Hach meter, calibrated at 06:15 on sampling days.

| Date | Totalizer at 07:00 next day, gal | In-line pH, low to high; grab at sampling | Notes |
| --- | --- | --- | --- |
| 07/01/2026 Wed | 4,888,995 | 7.2 to 7.6 | Normal operation. Chrome line running two shifts. |
| 07/02/2026 Thu | 4,928,908 | 7.3 to 7.6 | Normal operation. Polymer drum changed on the clarifier feed. |
| 07/03/2026 Fri | 4,928,908 |  | Plant closed, Independence Day observed. No discharge. |
| 07/04/2026 Sat | 4,930,795 |  | Weekend, no production; sump flow only. |
| 07/05/2026 Sun | 4,934,115 |  | Weekend, no production; sump flow only. |
| 07/06/2026 Mon | 4,966,879 | 7.4 to 7.8 | Normal operation. Composite sampler programmed for the 07/07 event and started at 06:40. |
| 07/07/2026 Tue | 5,005,480 | 7.0 to 7.7; grab 7.2 | Routine sampling event VP-260707, grab pH 7.2 at 06:40. Found the sampler dead on the 05:30 round. The GFI outlet had tripped at 15:10 on 07/06, and the bottle holds 9 aliquots, all from 06:40 to 15:10. Cyanide grab taken at 06:40. Iced the bottle as it was and sent it on the chain of custody. Outlet reset. |
| 07/08/2026 Wed | 5,040,060 | 6.8 to 7.4 | Normal operation. Caustic delivery, 2,200 gallons to the day tank, bill of lading in the binder. |
| 07/09/2026 Thu | 5,073,651 | 7.3 to 7.9 | Normal operation. Clarifier rake checked on the noon round. |
| 07/10/2026 Fri | 5,109,294 | 7.4 to 8.2 | Normal operation. Sampler tubing replaced ahead of the next event. |
| 07/11/2026 Sat | 5,111,030 |  | Weekend, no production; sump flow only. |
| 07/12/2026 Sun | 5,113,301 |  | Weekend, no production; sump flow only. |
| 07/13/2026 Mon | 5,144,730 | 7.2 to 7.6 | Normal operation. Sludge hauled by Kent County Disposal, 4.1 tons on the manifest. |
| 07/14/2026 Tue | 5,182,044 | 7.2 to 7.6 | Normal operation. Sludge press run. |
| 07/15/2026 Wed | 5,214,542 | 6.9 to 7.3 | Normal operation. Ferric feed pump seal replaced, back in service by 10:15. RT-2 level float stuck at 13:20, and the rinse tank went over to the floor trench. Sump valved to the equalization tank, and the trench was pumped back to treatment by 13:50 with nothing to the sewer connection. Float freed and tested. |
| 07/16/2026 Thu | 5,244,482 | 7.0 to 7.7 | Normal operation. Hach meter probe replaced; calibrated at 06:15 with the pH 7 and pH 10 buffers. |
| 07/17/2026 Fri | 30,947 | 6.9 to 7.6 | Normal operation. Effluent meter chart roll changed. Totalizer register replaced by the meter service at 07:05 after the 07:00 read; old register removed reading 5,244,482, new register installed reading 0. |
| 07/18/2026 Sat | 33,477 |  | Weekend, no production; sump flow only. |
| 07/19/2026 Sun | 36,718 |  | Weekend, no production; sump flow only. |
| 07/20/2026 Mon | 63,743 | 7.3 to 7.6 | Normal operation. Composite sampler programmed for the 07/21 event. |
| 07/21/2026 Tue | 103,622 | 7.4 to 8.5; grab 8.4 | Routine sampling event VP-260721, grab pH 8.4 at 06:30. 26 aliquots in the bottle. |
| 07/22/2026 Wed | 136,325 | 7.5 to 9.0 | Normal operation. Caustic feed running high in the morning; meter settled by 09:00. |
| 07/23/2026 Thu | 176,511 | 7.3 to 7.7 | Normal operation. Caustic day tank refilled from the bulk tank. Copper test kit on a clarifier grab read about 4 mg/L, so the ferric dose was raised. |
| 07/24/2026 Fri | 216,356 | 7.3 to 8.0 | Normal operation. Chrome reduction ORP probe cleaned. |
| 07/25/2026 Sat | 220,335 |  | Weekend, no production; sump flow only. |
| 07/26/2026 Sun | 223,792 |  | Weekend, no production; sump flow only. |
| 07/27/2026 Mon | 262,703 | 7.3 to 7.9 | Normal operation. Weekly walk-down of the trench and the sump with maintenance; float on RT-2 tested. |
| 07/28/2026 Tue | 307,583 | 6.8 to 7.5 | Normal operation. Zinc line on two shifts for the Kentwood order. |
| 07/29/2026 Wed | 336,064 | 7.1 to 7.5 | Normal operation. Polymer drum changed. |
| 07/30/2026 Thu | 365,173 | 6.9 to 7.6 | Normal operation. Sludge press cloths washed. |
| 07/31/2026 Fri | 402,867 | 7.4 to 8.1 | Normal operation. Month's charts pulled and filed in the binder. Called Renee Castellanos at the City at 09:40 on the 07/21 copper in yesterday's lab report. |

Operator's end-of-month note. Nothing went around the clarifier this month. The chart binder is up to date through the 31st.