Vandeveer Plating LLC - pretreatment system operator log, September 2026

Kept by Luis Baranski, wastewater treatment operator. The Outfall 001 totalizer sits on the clarifier effluent line, ahead of the sewer connection, and its register is read at 07:00 each morning. The reading on a line is the register at 07:00 the following morning, so a day's flow is that reading less the one before it. Register at 07:00 on 09/01/2026: 1,173,773 gallons. In-line pH is the low and the high from the effluent meter chart for the day; grab pH at sampling with the Hach meter, calibrated at 06:15 on sampling days.

| Date | Totalizer at 07:00 next day, gal | In-line pH, low to high; grab at sampling | Notes |
| --- | --- | --- | --- |
| 09/01/2026 Tue | 1,206,477 | 7.1 to 7.6 | Normal operation. Chrome line running two shifts. |
| 09/02/2026 Wed | 1,247,070 | 7.0 to 7.5 | Normal operation. |
| 09/03/2026 Thu | 1,279,366 | 7.4 to 8.1 | Polymer feed pump replaced; clarifier effluent clear by 10:30. |
| 09/04/2026 Fri | 1,317,021 | 7.2 to 7.6 | Normal operation. |
| 09/05/2026 Sat | 1,320,630 |  | Weekend, no production; sump flow only. |
| 09/06/2026 Sun | 1,322,605 |  | Weekend, no production; sump flow only. |
| 09/07/2026 Mon | 1,322,605 |  | Plant closed, Labor Day. No discharge. |
| 09/08/2026 Tue | 1,357,287 | 7.3 to 7.8 | Normal operation. Composite sampler programmed for the 09/09 event. |
| 09/09/2026 Wed | 1,400,937 | 7.2 to 8.0; grab 7.9 | Rinse tank RT-4 on the zinc line overflowed at 07:50 when the level float stuck; rinse water went to the floor trench and the sump pumped it to the sewer connection, downstream of the clarifier and of the totalizer, for about 35 minutes before the line was shut. Estimated 2,900 gallons bypassed treatment. Composite sample VP-260909 was running through the event, 27 aliquots in the bottle. Told Gordon at 08:30. |
| 09/10/2026 Thu | 1,432,667 | 7.5 to 8.1 | Called the City Pretreatment Coordinator at 16:30 about the 09/09 overflow; left the details with Renee Castellanos. RT-4 float replaced. |
| 09/11/2026 Fri | 1,461,510 | 6.0 to 7.4 | Normal operation. In-line meter touched 6.0 at 05:40 on start-up before the caustic feed caught up. Grab pH 7.6 at 09:00 as a check after the overflow. |
| 09/12/2026 Sat | 1,464,312 |  | Weekend, no production; sump flow only. |
| 09/13/2026 Sun | 1,468,092 |  | Weekend, no production; sump flow only. |
| 09/14/2026 Mon | 1,505,401 | 6.5 to 7.2 | Written overflow report signed by Gordon and emailed to the City at 15:10. |
| 09/15/2026 Tue | 1,540,238 | 7.0 to 7.6 | Lab report GLA-26-1811 received for VP-260909; zinc composite 3.14 mg/L. Gordon told; resample scheduled. |
| 09/16/2026 Wed | 1,580,202 | 7.1 to 7.7 | Normal operation. Called Renee Castellanos at the City at 10:05 on the zinc result. |
| 09/17/2026 Thu | 1,608,512 | 5.8 to 7.2 | In-line pH meter recorded 5.8 from 14:10 to 14:55 during an acid dump from the pickle tank; caustic feed increased and pH back to 6.9 by 15:00. Grab check at 15:05 read 6.9. Reported to Gordon; called Renee Castellanos at the City at 15:20 with the times and the cause. |
| 09/18/2026 Fri | 1,641,947 | 7.4 to 8.0 | Normal operation. |
| 09/19/2026 Sat | 1,646,101 |  | Weekend, no production; sump flow only. |
| 09/20/2026 Sun | 1,649,973 |  | Weekend, no production; sump flow only. |
| 09/21/2026 Mon | 1,690,504 | 7.6 to 8.2 | Normal operation. Written report on the 09/17 pH excursion signed by Gordon and emailed to the City at 10:40. Composite sampler programmed for the 09/22 event. |
| 09/22/2026 Tue | 1,724,632 | 7.0 to 7.5; grab 7.3 | Routine sampling event VP-260922, grab pH 7.3 at 06:35. 24 aliquots in the bottle. |
| 09/23/2026 Wed | 1,752,661 | 7.1 to 7.6; grab 7.4 | Resample VP-260923 collected at 07:05 at Gordon's request, metals composite only, 25 aliquots. Grab pH 7.4. |
| 09/24/2026 Thu | 1,780,577 | 7.0 to 7.5 | Normal operation. Copper test kit on an Outfall 001 grab at 10:15 read 3.9 mg/L; ferric dose held. |
| 09/25/2026 Fri | 1,819,521 | 6.9 to 7.4 | Normal operation. |
| 09/26/2026 Sat | 1,823,199 |  | Weekend, no production; sump flow only. |
| 09/27/2026 Sun | 1,825,943 |  | Weekend, no production; sump flow only. |
| 09/28/2026 Mon | 1,860,669 | 7.3 to 7.8 | Normal operation. Sludge press run. |
| 09/29/2026 Tue | 1,891,352 | 7.4 to 7.9 | Normal operation. |
| 09/30/2026 Wed | 1,925,843 | 7.1 to 7.6 | Normal operation. |

Operator's end-of-month note. The RT-4 overflow on the 9th is the only event this month that went around the clarifier. The pickle tank acid dump on the 17th did not leave the treatment system, but the effluent meter chart shows the 5.8 reading for 45 minutes and the chart is filed with this log. Both are in the chart binder for the City's inspection.