## SMR Q3
SELF-MONITORING REPORT, THIRD QUARTER 2026 (JULY 1 THROUGH SEPTEMBER 30, 2026)
Permittee: Vandeveer Plating LLC, 2140 Chicago Drive SW, Wyoming, Michigan 49519
Wastewater Discharge Permit No. IP-0421, City of Wyoming Clean Water Plant, Industrial Pretreatment Program
Report prepared October 12, 2026 for the Plant Manager's signature. Sampling point: Outfall 001, pretreatment system effluent. Report format per Attachment B; due to the City by October 15, 2026 under Section 3.1.
JULY 2026
PARAMETER | DAILY MAXIMUM LIMIT MG/L | MONTHLY AVERAGE LIMIT MG/L | VALID SAMPLES | REQUIRED | MONTHLY AVERAGE MG/L | DAILY MAXIMUM MG/L | MONTHLY AVERAGE MET | DAILY MAXIMUM MET | FREQUENCY MET
Cadmium, total | 0.11 | 0.07 | 1 | 2 | 0 | 0 | Met | Met | Below frequency
Chromium, total | 2.77 | 1.71 | 1 | 2 | 1.21 | 1.21 | Met | Met | Below frequency
Copper, total | 3.38 | 2.07 | 1 | 2 | 4.09 | 4.09 | Exceeded | Exceeded | Below frequency
Nickel, total | 3.98 | 2.38 | 1 | 2 | 1.57 | 1.57 | Met | Met | Below frequency
Zinc, total | 2.61 | 1.48 | 1 | 2 | 1.27 | 1.27 | Met | Met | Below frequency
Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.31 | 0.35 | Met | Met | Met
pH, standard units, grabs at sampling | 6.0 to 9.0 | not applicable | 2 | 2 | 7.2 | 8.4 | In-line meter: none reported | Met | Met
Flow, gallons per day | 45000 | not applicable | daily | daily |  | no day above the limit per the plant manager's review of the operator logs | not applicable | Met | Met
AUGUST 2026
PARAMETER | DAILY MAXIMUM LIMIT MG/L | MONTHLY AVERAGE LIMIT MG/L | VALID SAMPLES | REQUIRED | MONTHLY AVERAGE MG/L | DAILY MAXIMUM MG/L | MONTHLY AVERAGE MET | DAILY MAXIMUM MET | FREQUENCY MET
Cadmium, total | 0.11 | 0.07 | 2 | 2 | 0.007 | 0.014 | Met | Met | Met
Chromium, total | 2.77 | 1.71 | 2 | 2 | 0.7 | 0.74 | Met | Met | Met
Copper, total | 3.38 | 2.07 | 2 | 2 | 4.24 | 4.33 | Exceeded | Exceeded | Met
Nickel, total | 3.98 | 2.38 | 1 | 2 | 2.61 | 2.61 | Exceeded | Met | Below frequency
Zinc, total | 2.61 | 1.48 | 2 | 2 | 1.035 | 1.18 | Met | Met | Met
Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.24 | 0.29 | Met | Met | Met
pH, standard units, grabs at sampling | 6.0 to 9.0 | not applicable | 2 | 2 | 6.8 | 7.5 | In-line meter: none reported | Met | Met
Flow, gallons per day | 45000 | not applicable | daily | daily |  | no day above the limit per the plant manager's review of the operator logs | not applicable | Met | Met
SEPTEMBER 2026
PARAMETER | DAILY MAXIMUM LIMIT MG/L | MONTHLY AVERAGE LIMIT MG/L | VALID SAMPLES | REQUIRED | MONTHLY AVERAGE MG/L | DAILY MAXIMUM MG/L | MONTHLY AVERAGE MET | DAILY MAXIMUM MET | FREQUENCY MET
Cadmium, total | 0.11 | 0.07 | 3 | 2 | 0.004 | 0.012 | Met | Met | Met
Chromium, total | 2.77 | 1.71 | 3 | 2 | 0.697 | 1.02 | Met | Met | Met
Copper, total | 3.38 | 2.07 | 3 | 2 | 2.053 | 2.96 | Met | Met | Met
Nickel, total | 3.98 | 2.38 | 3 | 2 | 1.15 | 1.36 | Met | Met | Met
Zinc, total | 2.61 | 1.48 | 3 | 2 | 1.653 | 3.14 | Exceeded | Exceeded | Met
Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.325 | 0.41 | Met | Met | Met
pH, standard units, grabs at sampling | 6.0 to 9.0 | not applicable | 3 | 2 | 7.3 | 7.9 | In-line meter: one excursion, 09/17/2026; the 6.0 low of 09/11/2026 is inside the range | Exceeded | Met
Flow, gallons per day | 45000 | not applicable | daily | daily |  | 47300 | not applicable | Exceeded | Met
VIOLATIONS IN THE QUARTER
DATE | PARAMETER OR CONDITION | VALUE | LIMITATION | PERMIT SECTION | CAUSE AS KNOWN
07/21/2026 | Copper, daily maximum, sample VP-260721 | 4.09 | 3.38 mg/L | Part I | Copper carryover from the plating line; treatment chemistry under review by the plant
July 2026 | Copper, monthly average, one valid sample | 4.09 | 2.07 mg/L | Part I | The July 21 result stands alone after the July 7 sample's metals were analyzed outside the holding period
July 2026 | Cadmium, chromium, copper, nickel and zinc, monitoring frequency | 1 | 2 valid samples | Section 2.3 | Metals of sample VP-260707 analyzed 08/06/2026, 30 days after collection, outside the 28-day holding period; the laboratory reported the month on 08/07/2026 after it had ended, so no replacement could be collected
08/11/2026 | Copper, daily maximum, sample VP-260811 | 4.33 | 3.38 mg/L | Part I | Copper carryover from the plating line
08/25/2026 | Copper, daily maximum, sample VP-260825 | 4.15 | 3.38 mg/L | Part I | Copper carryover from the plating line
August 2026 | Copper, monthly average | 4.24 | 2.07 mg/L | Part I | Same cause as the daily maximum exceedances
August 2026 | Nickel, monthly average, one valid sample | 2.61 | 2.38 mg/L | Part I | Nickel result of 08/11/2026 stands alone after the 08/25/2026 nickel result was analyzed 34 days after collection, outside the holding period
August 2026 | Nickel, monitoring frequency | 1 | 2 valid samples | Section 2.3 | Nickel of sample VP-260825 analyzed 09/28/2026, outside the 28-day holding period; no replacement before month end
09/09/2026 | Zinc, daily maximum, sample VP-260909 | 3.14 | 2.61 mg/L | Part I | Rinse tank RT-4 overflow during the composite
September 2026 | Zinc, monthly average | 1.653 | 1.48 mg/L | Part I | The 09/09/2026 result carries the month
09/09/2026 | Flow, daily, worked from the totalizer register | 47300 | 45,000 gallons per day | Part I | Rinse tank RT-4 overflow, about 2,900 gallons to the sewer around treatment
09/09/2026 | Bypass of the pretreatment system, 07:50 for about 35 minutes | 2,900 gallons | No bypass | Section 4.1 | Level float on RT-4 stuck; float replaced 09/10/2026
09/10/2026 | Telephone notice of the bypass made at 16:30, after the 24-hour period | 32 hours 40 minutes after the event | 24 hours | Section 3.2 | Notice made the next afternoon
09/17/2026 | pH, in-line meter, 14:10 to 14:55 | 5.8 | 6.0 to 9.0 | Section 2.4 and Section 4.2 | Acid dump from the pickle tank; caustic feed increased, pH 6.9 by 15:00; called in at 15:20 and reported in writing 09/21/2026
07/31/2026 | Telephone notice of the copper daily maximum exceedance reported 07/30/2026 not made | none made | 24 hours | Section 3.2 | No call in the City's telephone log after the laboratory report; the laboratory's copy of the report to the City is not a notice under Section 3.2
08/21/2026 | Telephone notice of the copper daily maximum exceedance reported 08/20/2026 not made | none made | 24 hours | Section 3.2 | No call in the City's telephone log after the laboratory report; the laboratory's copy of the report to the City is not a notice under Section 3.2
09/05/2026 | Telephone notice of the copper daily maximum exceedance reported 09/04/2026 not made | none made | 24 hours | Section 3.2 | No call in the City's telephone log after the laboratory report; the laboratory's copy of the report to the City is not a notice under Section 3.2
SIX-MONTH SIGNIFICANT NONCOMPLIANCE EVALUATION, APRIL THROUGH SEPTEMBER 2026
Copper measurements in the period, valid results only | 12
Copper measurements above the technical review criterion threshold | 4
Share above the technical review criterion threshold, percent | 33.3
Threshold for the technical review criterion test, percent | 33
Copper significant noncompliance status | Significant noncompliance
No other parameter reaches either threshold; see the evaluation tab for every parameter. The second quarter report reached the City on 07/14/2026 against its 07/15/2026 due date, so the report arm of Section 3.4 is not triggered.
CERTIFICATION
I certify under penalty of law that this document and all attachments were prepared under my direction or supervision in accordance with a system designed to assure that qualified personnel properly gather and evaluate the information submitted. Based on my inquiry of the person or persons who manage the system, or those persons directly responsible for gathering the information, the information submitted is, to the best of my knowledge and belief, true, accurate and complete. I am aware that there are significant penalties for submitting false information, including the possibility of fine and imprisonment for knowing violations.
Authorized representative: ______________________________
Name: Gordon Pfeiffer
Title: Plant Manager
Date: ______________

## Parameters
Permit limitations and computation parameters, Wastewater Discharge Permit IP-0421
PARAMETER | DAILY MAXIMUM MG/L | MONTHLY AVERAGE MG/L | MDL MG/L | SOURCE
Cadmium, total | 0.11 | 0.07 | 0.005 | Part I of the permit; MDL from the laboratory's Methods tab
Chromium, total | 2.77 | 1.71 | 0.01 | Part I of the permit; MDL from the laboratory's Methods tab
Copper, total | 3.38 | 2.07 | 0.01 | Part I of the permit; MDL from the laboratory's Methods tab
Nickel, total | 3.98 | 2.38 | 0.02 | Part I of the permit; MDL from the laboratory's Methods tab
Zinc, total | 2.61 | 1.48 | 0.02 | Part I of the permit; MDL from the laboratory's Methods tab
Cyanide, total | 1.2 | 0.65 | 0.005 | Part I of the permit; MDL from the laboratory's Methods tab
OTHER PARAMETER | VALUE |  |  | SOURCE
Daily flow limit, gallons per day | 45000 |  |  | Part I of the permit
pH range, standard units, lower bound | 6 |  |  | Part I of the permit
pH range, standard units, upper bound | 9 |  |  | Part I of the permit
Required valid samples per parameter per month | 2 |  |  | Section 2.1 of the permit
Technical review criterion for metals and cyanide | 1.2 |  |  | Section 3.4 of the permit
Chronic significant noncompliance threshold, percent of measurements | 66 |  |  | Section 3.4 of the permit
Technical review criterion significant noncompliance threshold, percent of measurements | 33 |  |  | Section 3.4 of the permit
Telephone notice, hours after becoming aware | 24 |  |  | Section 3.2 of the permit
Written report, days after the event | 5 |  |  | Section 3.2 of the permit
Resample, days after becoming aware of a daily maximum exceedance | 30 |  |  | Section 3.3 of the permit
Self-monitoring report due, day of the month after the quarter | 15 |  |  | Section 3.1 of the permit
Holding period, total metals, days from collection | 28 |  |  | Section 2.3 of the permit (40 CFR Part 136); the period the laboratory's chain of custody log states
Holding period, total cyanide, days from collection | 14 |  |  | Section 2.3 of the permit (40 CFR Part 136); the period the laboratory's chain of custody log states

## Lab Data
Laboratory results April through September 2026, Outfall 001, as reported (lab_results_apr_sep2026.xlsx)
RESULT and QUAL are the laboratory's figures as typed; the ANALYZED dates are from the laboratory's chain of custody log, and the SERIAL columns carry the same dates as Excel serials for the day count. VALID is N for a result not sampled (NS) or analyzed more than the holding period after collection, Section 2.3 and Parameters rows 23 and 24. TREATED carries a U result at zero for averaging, Section 2.2.
SAMPLE ID | COLLECTED | MONTH | TYPE | Cd RESULT | Cd QUAL | Cd VALID | Cd TREATED | Cr RESULT | Cr QUAL | Cr VALID | Cr TREATED | Cu RESULT | Cu QUAL | Cu VALID | Cu TREATED | Ni RESULT | Ni QUAL | Ni VALID | Ni TREATED | Zn RESULT | Zn QUAL | Zn VALID | Zn TREATED | CN RESULT | CN QUAL | CN VALID | CN TREATED | FIELD PH | LAB REPORT DATE | METALS ANALYZED | NICKEL ANALYZED | CYANIDE ANALYZED | METALS HOLD DAYS | NICKEL HOLD DAYS | CYANIDE HOLD DAYS | COLLECTED, SERIAL | METALS ANALYZED, SERIAL | NICKEL ANALYZED, SERIAL | CYANIDE ANALYZED, SERIAL
VP-260407 | 04/07/2026 | Apr | Routine | 0.005 | U | Y | 0 | 0.62 |  | Y | 0.62 | 1.84 |  | Y | 1.84 | 0.91 |  | Y | 0.91 | 0.74 |  | Y | 0.74 | 0.18 |  | Y | 0.18 | 7.4 | 04/17/2026 | 04/11/2026 | 04/11/2026 | 04/12/2026 | 4 | 4 | 5 | 46119 | 46123 | 46123 | 46124
VP-260421 | 04/21/2026 | Apr | Routine | 0.012 |  | Y | 0.012 | 0.48 |  | Y | 0.48 | 3.62 |  | Y | 3.62 | 1.44 |  | Y | 1.44 | 1.12 |  | Y | 1.12 | 0.31 |  | Y | 0.31 | 7.1 | 04/30/2026 | 04/25/2026 | 04/25/2026 | 04/23/2026 | 4 | 4 | 2 | 46133 | 46137 | 46137 | 46135
VP-260505 | 05/05/2026 | May | Routine | 0.005 | U | Y | 0 | 1.13 |  | Y | 1.13 | 4.21 |  | Y | 4.21 | 0.77 |  | Y | 0.77 | 0.68 |  | Y | 0.68 | 0.22 |  | Y | 0.22 | 8.2 | 05/14/2026 | 05/08/2026 | 05/08/2026 | 05/10/2026 | 3 | 3 | 5 | 46147 | 46150 | 46150 | 46152
VP-260519 | 05/19/2026 | May | Routine | 0.005 | U | Y | 0 | 0.71 |  | Y | 0.71 | 1.95 |  | Y | 1.95 | 1.68 |  | Y | 1.68 | 0.95 |  | Y | 0.95 | 0.008 | J | Y | 0.008 | 7.6 | 05/29/2026 | 05/26/2026 | 05/26/2026 | 05/25/2026 | 7 | 7 | 6 | 46161 | 46168 | 46168 | 46167
VP-260602 | 06/02/2026 | Jun | Routine | 0.019 |  | Y | 0.019 | 0.55 |  | Y | 0.55 | 2.4 |  | Y | 2.4 | 1.05 |  | Y | 1.05 | 1.31 |  | Y | 1.31 | 0.71 |  | Y | 0.71 | 6.9 | 06/12/2026 | 06/08/2026 | 06/08/2026 | 06/07/2026 | 6 | 6 | 5 | 46175 | 46181 | 46181 | 46180
VP-260616 | 06/16/2026 | Jun | Routine | 0.005 | U | Y | 0 | 0.93 |  | Y | 0.93 | 3.97 |  | Y | 3.97 | 0.83 |  | Y | 0.83 | 0.82 |  | Y | 0.82 | 0.44 |  | Y | 0.44 | 7.8 | 06/26/2026 | 07/13/2026 | 07/13/2026 | 06/18/2026 | 27 | 27 | 2 | 46189 | 46216 | 46216 | 46191
VP-260707 | 07/07/2026 | Jul | Routine | 0.005 | U | N | 0 | 0.87 |  | N | 0.87 | 1.77 |  | N | 1.77 | 1.22 |  | N | 1.22 | 1.06 |  | N | 1.06 | 0.27 |  | Y | 0.27 | 7.2 | 08/07/2026 | 08/06/2026 | 08/06/2026 | 07/13/2026 | 30 | 30 | 6 | 46210 | 46240 | 46240 | 46216
VP-260721 | 07/21/2026 | Jul | Routine | 0.005 | U | Y | 0 | 1.21 |  | Y | 1.21 | 4.09 |  | Y | 4.09 | 1.57 |  | Y | 1.57 | 1.27 |  | Y | 1.27 | 0.35 |  | Y | 0.35 | 8.4 | 07/30/2026 | 07/26/2026 | 07/26/2026 | 07/25/2026 | 5 | 5 | 4 | 46224 | 46229 | 46229 | 46228
VP-260811 | 08/11/2026 | Aug | Routine | 0.014 |  | Y | 0.014 | 0.66 |  | Y | 0.66 | 4.33 |  | Y | 4.33 | 2.61 |  | Y | 2.61 | 0.89 |  | Y | 0.89 | 0.19 |  | Y | 0.19 | 6.8 | 08/20/2026 | 08/15/2026 | 08/15/2026 | 08/14/2026 | 4 | 4 | 3 | 46245 | 46249 | 46249 | 46248
VP-260825 | 08/25/2026 | Aug | Routine | 0.005 | U | Y | 0 | 0.74 |  | Y | 0.74 | 4.15 |  | Y | 4.15 | 1.9 |  | N | 1.9 | 1.18 |  | Y | 1.18 | 0.29 |  | Y | 0.29 | 7.5 | 09/04/2026 | 08/29/2026 | 09/28/2026 | 08/27/2026 | 4 | 34 | 2 | 46259 | 46263 | 46293 | 46261
VP-260909 | 09/09/2026 | Sep | Routine | 0.012 |  | Y | 0.012 | 1.02 |  | Y | 1.02 | 2.96 |  | Y | 2.96 | 1.36 |  | Y | 1.36 | 3.14 |  | Y | 3.14 | 0.41 |  | Y | 0.41 | 7.9 | 09/15/2026 | 09/12/2026 | 09/12/2026 | 09/22/2026 | 3 | 3 | 13 | 46274 | 46277 | 46277 | 46287
VP-260922 | 09/22/2026 | Sep | Routine | 0.005 | U | Y | 0 | 0.58 |  | Y | 0.58 | 1.68 |  | Y | 1.68 | 0.98 |  | Y | 0.98 | 0.94 |  | Y | 0.94 | 0.24 |  | Y | 0.24 | 7.3 | 10/01/2026 | 09/30/2026 | 09/30/2026 | 09/28/2026 | 8 | 8 | 6 | 46287 | 46295 | 46295 | 46293
VP-260923 | 09/23/2026 | Sep | Resample | 0.005 | U | Y | 0 | 0.49 |  | Y | 0.49 | 1.52 |  | Y | 1.52 | 1.11 |  | Y | 1.11 | 0.88 |  | Y | 0.88 |  | NS | N | 0 | 7.4 | 10/01/2026 | 09/26/2026 | 09/26/2026 | not collected | 3 | 3 | not collected | 46288 | 46291 | 46291 | not collected
Formulas:
METALS HOLD DAYS = DAYS([METALS ANALYZED, SERIAL],[COLLECTED, SERIAL])
NICKEL HOLD DAYS = DAYS([NICKEL ANALYZED, SERIAL],[COLLECTED, SERIAL])
CYANIDE HOLD DAYS = DAYS([CYANIDE ANALYZED, SERIAL],[COLLECTED, SERIAL])

## Monthly Stats
Monthly averages and daily maximums by parameter, April through September 2026
Monthly average is the arithmetic mean of the valid results in the month, resamples included, non-detects at zero (Section 2.2); daily maximum is the highest valid result in the month. A result analyzed outside its holding period is not a valid sample, and a month with fewer valid samples than required is monitored below frequency (Section 2.3).
MONTH | PARAMETER | DAILY MAXIMUM LIMIT | MONTHLY AVERAGE LIMIT | VALID SAMPLES | REQUIRED | MONTHLY AVERAGE | DAILY MAXIMUM | MONTHLY AVERAGE STATUS | DAILY MAXIMUM STATUS | FREQUENCY STATUS
Apr | Cadmium, total | 0.11 | 0.07 | 2 | 2 | 0.006 | 0.012 | Met | Met | Met
Apr | Chromium, total | 2.77 | 1.71 | 2 | 2 | 0.55 | 0.62 | Met | Met | Met
Apr | Copper, total | 3.38 | 2.07 | 2 | 2 | 2.73 | 3.62 | Exceeded | Exceeded | Met
Apr | Nickel, total | 3.98 | 2.38 | 2 | 2 | 1.175 | 1.44 | Met | Met | Met
Apr | Zinc, total | 2.61 | 1.48 | 2 | 2 | 0.93 | 1.12 | Met | Met | Met
Apr | Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.245 | 0.31 | Met | Met | Met
May | Cadmium, total | 0.11 | 0.07 | 2 | 2 | 0 | 0 | Met | Met | Met
May | Chromium, total | 2.77 | 1.71 | 2 | 2 | 0.92 | 1.13 | Met | Met | Met
May | Copper, total | 3.38 | 2.07 | 2 | 2 | 3.08 | 4.21 | Exceeded | Exceeded | Met
May | Nickel, total | 3.98 | 2.38 | 2 | 2 | 1.225 | 1.68 | Met | Met | Met
May | Zinc, total | 2.61 | 1.48 | 2 | 2 | 0.815 | 0.95 | Met | Met | Met
May | Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.114 | 0.22 | Met | Met | Met
Jun | Cadmium, total | 0.11 | 0.07 | 2 | 2 | 0.01 | 0.019 | Met | Met | Met
Jun | Chromium, total | 2.77 | 1.71 | 2 | 2 | 0.74 | 0.93 | Met | Met | Met
Jun | Copper, total | 3.38 | 2.07 | 2 | 2 | 3.185 | 3.97 | Exceeded | Exceeded | Met
Jun | Nickel, total | 3.98 | 2.38 | 2 | 2 | 0.94 | 1.05 | Met | Met | Met
Jun | Zinc, total | 2.61 | 1.48 | 2 | 2 | 1.065 | 1.31 | Met | Met | Met
Jun | Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.575 | 0.71 | Met | Met | Met
Jul | Cadmium, total | 0.11 | 0.07 | 1 | 2 | 0 | 0 | Met | Met | Below frequency
Jul | Chromium, total | 2.77 | 1.71 | 1 | 2 | 1.21 | 1.21 | Met | Met | Below frequency
Jul | Copper, total | 3.38 | 2.07 | 1 | 2 | 4.09 | 4.09 | Exceeded | Exceeded | Below frequency
Jul | Nickel, total | 3.98 | 2.38 | 1 | 2 | 1.57 | 1.57 | Met | Met | Below frequency
Jul | Zinc, total | 2.61 | 1.48 | 1 | 2 | 1.27 | 1.27 | Met | Met | Below frequency
Jul | Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.31 | 0.35 | Met | Met | Met
Aug | Cadmium, total | 0.11 | 0.07 | 2 | 2 | 0.007 | 0.014 | Met | Met | Met
Aug | Chromium, total | 2.77 | 1.71 | 2 | 2 | 0.7 | 0.74 | Met | Met | Met
Aug | Copper, total | 3.38 | 2.07 | 2 | 2 | 4.24 | 4.33 | Exceeded | Exceeded | Met
Aug | Nickel, total | 3.98 | 2.38 | 1 | 2 | 2.61 | 2.61 | Exceeded | Met | Below frequency
Aug | Zinc, total | 2.61 | 1.48 | 2 | 2 | 1.035 | 1.18 | Met | Met | Met
Aug | Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.24 | 0.29 | Met | Met | Met
Sep | Cadmium, total | 0.11 | 0.07 | 3 | 2 | 0.004 | 0.012 | Met | Met | Met
Sep | Chromium, total | 2.77 | 1.71 | 3 | 2 | 0.697 | 1.02 | Met | Met | Met
Sep | Copper, total | 3.38 | 2.07 | 3 | 2 | 2.053 | 2.96 | Met | Met | Met
Sep | Nickel, total | 3.98 | 2.38 | 3 | 2 | 1.15 | 1.36 | Met | Met | Met
Sep | Zinc, total | 2.61 | 1.48 | 3 | 2 | 1.653 | 3.14 | Exceeded | Exceeded | Met
Sep | Cyanide, total | 1.2 | 0.65 | 2 | 2 | 0.325 | 0.41 | Met | Met | Met

## SNC Review
Significant noncompliance evaluation, April 1 through September 30, 2026, Section 3.4 of the permit
Every valid result in the period is a measurement, resamples included. Each measurement is compared with the daily maximum limitation and with the limitation multiplied by the technical review criterion of 1.2.
PARAMETER | MEASUREMENTS | DAILY MAXIMUM LIMIT | TRC MULTIPLIER | TRC THRESHOLD MG/L | ABOVE THE LIMIT | SHARE ABOVE THE LIMIT PCT | ABOVE THE TRC THRESHOLD | SHARE ABOVE THE TRC THRESHOLD PCT | CHRONIC AT 66 PCT | TRC AT 33 PCT | SIGNIFICANT NONCOMPLIANCE | CHRONIC THRESHOLD PCT | TRC THRESHOLD PCT
Cadmium, total | 12 | 0.11 | 1.2 | 0.132 | 0 | 0 | 0 | 0 | No | No | Not in significant noncompliance | 66 | 33
Chromium, total | 12 | 2.77 | 1.2 | 3.324 | 0 | 0 | 0 | 0 | No | No | Not in significant noncompliance | 66 | 33
Copper, total | 12 | 3.38 | 1.2 | 4.056 | 6 | 50 | 4 | 33.3 | No | Yes | Significant noncompliance | 66 | 33
Nickel, total | 11 | 3.98 | 1.2 | 4.776 | 0 | 0 | 0 | 0 | No | No | Not in significant noncompliance | 66 | 33
Zinc, total | 12 | 2.61 | 1.2 | 3.132 | 1 | 8.3 | 1 | 8.3 | No | No | Not in significant noncompliance | 66 | 33
Cyanide, total | 12 | 1.2 | 1.2 | 1.44 | 0 | 0 | 0 | 0 | No | No | Not in significant noncompliance | 66 | 33
A parameter in significant noncompliance is published in the City's annual notice and goes to the enforcement response plan (Section 3.4). Copper is the one parameter over the technical review criterion threshold, and only because the July 7 sample's metals are not valid measurements.
REPORT DUE IN THE PERIOD | DUE | RECEIVED | 45-DAY ARM OF SECTION 3.4
Second quarter self-monitoring report (Section 3.1) | 07/15/2026 | 07/14/2026 | Not late
The received date is the Pretreatment Coordinator's, from her note of September 30, 2026.

## Flow Sep
Daily flow, September 2026, gallons, worked from the totalizer register readings in the operator log
The log carries the register at 07:00 the following morning; a day's flow is that reading less the one before it. The month's total is the end register less the start register.
DATE | REGISTER AT 07:00 NEXT DAY, GAL | DAILY FLOW, GAL | ABOVE LIMIT
Register at 07:00 on 09/01/2026 | 6418255
09/01/2026 | 6450959 | 32704 | No
09/02/2026 | 6491552 | 40593 | No
09/03/2026 | 6523848 | 32296 | No
09/04/2026 | 6561503 | 37655 | No
09/05/2026 | 6565112 | 3609 | No
09/06/2026 | 6567087 | 1975 | No
09/07/2026 | 6567087 | 0 | No
09/08/2026 | 6601769 | 34682 | No
09/09/2026 | 6649069 | 47300 | Yes
09/10/2026 | 6680799 | 31730 | No
09/11/2026 | 6709642 | 28843 | No
09/12/2026 | 6712444 | 2802 | No
09/13/2026 | 6716224 | 3780 | No
09/14/2026 | 6753533 | 37309 | No
09/15/2026 | 6788370 | 34837 | No
09/16/2026 | 6828334 | 39964 | No
09/17/2026 | 6856644 | 28310 | No
09/18/2026 | 6890079 | 33435 | No
09/19/2026 | 6894233 | 4154 | No
09/20/2026 | 6898105 | 3872 | No
09/21/2026 | 6938636 | 40531 | No
09/22/2026 | 6972764 | 34128 | No
09/23/2026 | 7000793 | 28029 | No
09/24/2026 | 7028709 | 27916 | No
09/25/2026 | 7067653 | 38944 | No
09/26/2026 | 7071331 | 3678 | No
09/27/2026 | 7074075 | 2744 | No
09/28/2026 | 7108801 | 34726 | No
09/29/2026 | 7139484 | 30683 | No
09/30/2026 | 7173975 | 34491 | No
Highest daily flow in September | 47300
Days above the daily flow limit | 1
Total for the month, the end register less the start register | 755720
Sum of the daily flows, which ties to the register total | 755720

## Notifications
Notifications and resampling the quarter required, with the dates due and the dates done
EVENT | PERMIT SECTION | EVENT OR AWARENESS DATE | REQUIREMENT | DUE | DONE | STATUS
Rinse tank RT-4 overflow, a bypass of the pretreatment system, 09/09/2026 at 07:50 | Section 3.2 and Section 4.1 | 09/09/2026 07:50 | Telephone notice within 24 hours | 09/10/2026 07:50 | 09/10/2026 16:30 | Late
Rinse tank RT-4 overflow, written report | Section 3.2 | 09/09/2026 | Written report within 5 days | 09/14/2026 | 09/14/2026 | Met
In-line pH excursion of 09/17/2026, 14:10 to 14:55, called in as a discharge under Section 3.2 | Section 3.2 | 09/17/2026 14:10 | Telephone notice within 24 hours | 09/18/2026 14:10 | 09/17/2026 15:20 | Met
In-line pH excursion of 09/17/2026, written report | Section 3.2 | 09/17/2026 | Written report within 5 days | 09/22/2026 | 09/21/2026 | Met
Zinc daily maximum exceedance, sample VP-260909, 3.14 mg/L | Section 3.3 | 09/15/2026 (lab report) | Resample within 30 days | 10/15/2026 | 09/22/2026 and 09/23/2026 | Met
Copper daily maximum exceedance, sample VP-260721, 4.09 mg/L | Section 3.3 | 07/30/2026 (lab report) | Resample within 30 days; a routine sample in the period satisfies it | 08/29/2026 | 08/11/2026 routine sample | Met
Copper daily maximum exceedance, sample VP-260811, 4.33 mg/L | Section 3.3 | 08/20/2026 (lab report) | Resample within 30 days; a routine sample in the period satisfies it | 09/19/2026 | 08/25/2026 routine sample | Met
Copper daily maximum exceedance, sample VP-260825, 4.15 mg/L | Section 3.3 | 09/04/2026 (lab report) | Resample within 30 days; a routine sample in the period satisfies it | 10/04/2026 | 09/09/2026 routine sample | Met
Copper daily maximum exceedances of 07/21, 08/11 and 08/25, discharges exceeding a daily maximum | Section 3.2 | 07/30/2026, 08/20/2026, 09/04/2026 (lab reports) | Telephone notice within 24 hours of each report | 07/31/2026, 08/21/2026, 09/05/2026 | Not made; the City's telephone log for the quarter shows the calls of 09/10/2026 and 09/17/2026 only | Not made
Second quarter self-monitoring report | Section 3.1 and Section 3.4 | 06/30/2026 (quarter end) | Report in the Attachment B format by the 15th; 45 days late is significant noncompliance | 07/15/2026 | 07/14/2026, received by the City | Met
Third quarter self-monitoring report | Section 3.1 | 09/30/2026 (quarter end) | Report in the Attachment B format, signed | 10/15/2026 | Signing planned 10/13/2026 | Pending

## Note to Gordon
To: Gordon Pfeiffer, Plant Manager
Date: October 12, 2026
Re: Third quarter 2026 self-monitoring report, Permit IP-0421, before you sign
The overflow is not the quarter's only problem. The six-month review that Renee runs on the April through September results puts the plant in significant noncompliance for copper under Section 3.4: 4 of the 12 copper measurements since April exceed the daily maximum by more than the technical review criterion of 1.2, which is 33.3 percent against the 33 percent threshold, so the plant goes into the annual publication and the enforcement response plan on copper. The count is 12 rather than 13 because the July 7 sample's metals are not valid measurements, and that one reading is what puts the plant over the line.
The laboratory's chain of custody log shows the metals on sample VP-260707 of July 7 analyzed on August 6, 30 days after collection and outside the 28-day holding period for total metals, so under Section 2.3 that sample is not a valid sample for cadmium, chromium, copper, nickel or zinc. The laboratory did not flag it, and it shows only in the analysis dates. With the July 7 sample counted, the share would read 30.8 percent, and the plant would be clear. The permit does not allow it to be counted. The same test drops the August 25 nickel result, analyzed on September 28, 34 days after collection. The June 16 metals, analyzed on July 13 at 27 days, and the September 9 cyanide, analyzed on September 22 at 13 days, are inside their holding periods and stand.
July is reported as monitored below the required frequency for the five metals, since the laboratory reported the July 7 sample on August 7 after the month had ended and no replacement could be collected in July. The July copper monthly average therefore rests on the July 21 result alone, 4.09 mg/L against the 2.07 mg/L limit, and August's is 4.24 mg/L. Copper exceeded the daily maximum on July 21 at 4.09 mg/L, on August 11 at 4.33 mg/L, and on August 25 at 4.15 mg/L, against the 3.38 mg/L limit. September's copper average is 2.053 mg/L and meets the limit only because the resample of September 23 counts in the month's average, as Section 2.2 provides. Without the resample the September average would be 2.32 mg/L.
The September 9 overflow is a bypass under Section 4.1, and it is reported as one. Zinc on the composite that day was 3.14 mg/L against the 2.61 mg/L daily maximum, and that one result carries the September zinc average to 1.653 mg/L against the 1.48 mg/L monthly limit. The day's flow, worked from the totalizer register readings in Luis's log, is 47,300 gallons against the 45,000 gallon daily limit. The telephone notice to Renee was made at 16:30 on September 10, which is past the 24 hours Section 3.2 allows from the 07:50 event, so the late notice is reported as a violation of Section 3.2. The written report of September 14 was inside the five days.
The pH reading of 5.8 on the in-line meter on September 17, from 14:10 to 14:55 during the pickle tank acid dump, is a violation under Section 2.4 and Section 4.2 even though every grab at sampling was inside the range, and it is listed with its duration and cause. Luis's call to Renee at 15:20 the same afternoon and the written report of September 21 meet Section 3.2 on that event. The meter's low of 6.0 on the morning of September 11 is inside the range and is not a violation.
Nickel has a reporting problem in August. The August 25 nickel result is not valid under Section 2.3, so the August nickel average rests on the August 11 result alone, 2.61 mg/L against the 2.38 mg/L monthly limit, and August is reported as monitored below the required frequency for nickel, since no replacement sample was collected before the month ended. Not-detected results are carried at zero in the averages, as Section 2.2 directs, which is why the September cadmium average reads 0.004 mg/L rather than the detection limit.
Section 3.2 also calls for a telephone notice within 24 hours of becoming aware of any discharge exceeding a daily maximum, and Section 3.3 dates awareness to the laboratory report. Renee's telephone log for the quarter shows the calls of September 10 and September 17 and nothing after the July 30, August 20 or September 4 lab reports on the copper exceedances, and the laboratory's copies to Renee are not the telephone notice the section calls for. Those three are reported as violations of Section 3.2 in the violations table. The resample requirement of Section 3.3 is met on every exceedance: the zinc resample was due within 30 days of the September 15 lab report and was collected on September 22 and September 23, and each of the three copper exceedances was followed by a routine sample inside its 30-day period, which Section 3.3 accepts.
The second quarter report reached Renee on July 14 against its July 15 due date, so the report arm of Section 3.4 is not triggered, and no parameter other than copper reaches either threshold.
Two things the file leaves open. Whether Renee treats the laboratory's copies of the July and August reports as any notice at all is her call, and the report states the facts as the file shows them. The copper treatment itself is the plant's to fix, and the report states the cause only as far as the log and the lab results show it.