## Results
Great Lakes Analytical Laboratories - analytical results, client Vandeveer Plating LLC, sampling point Outfall 001 (pretreatment system effluent)
Results in mg/L. Qualifiers: NS = not sampled; U = not detected at the MDL shown on the Methods tab; J = detected between the MDL and the reporting limit, value estimated. Compiled from lab reports GLA-26-1187 through GLA-26-1904.
SAMPLE ID | COLLECTED | TIME | TYPE | Cd MG/L | Cd QUAL | Cr MG/L | Cr QUAL | Cu MG/L | Cu QUAL | Ni MG/L | Ni QUAL | Zn MG/L | Zn QUAL | CN MG/L | CN QUAL | FIELD PH | REPORT DATE
VP-260407 | 04/07/2026 | 06:40 | Routine | 0.005 | U | 0.62 |  | 1.84 |  | 0.91 |  | 0.74 |  | 0.18 |  | 7.4 | 04/17/2026
VP-260421 | 04/21/2026 | 06:35 | Routine | 0.012 |  | 0.48 |  | 3.62 |  | 1.44 |  | 1.12 |  | 0.31 |  | 7.1 | 04/30/2026
VP-260505 | 05/05/2026 | 06:50 | Routine | 0.005 | U | 1.13 |  | 4.21 |  | 0.77 |  | 0.68 |  | 0.22 |  | 8.2 | 05/14/2026
VP-260519 | 05/19/2026 | 06:45 | Routine | 0.005 | U | 0.71 |  | 1.95 |  | 1.68 |  | 0.95 |  | 0.008 | J | 7.6 | 05/29/2026
VP-260602 | 06/02/2026 | 06:40 | Routine | 0.019 |  | 0.55 |  | 2.4 |  | 1.05 |  | 1.31 |  | 0.71 |  | 6.9 | 06/12/2026
VP-260616 | 06/16/2026 | 06:55 | Routine | 0.005 | U | 0.93 |  | 3.97 |  | 0.83 |  | 0.82 |  | 0.44 |  | 7.8 | 06/26/2026
VP-260707 | 07/07/2026 | 06:40 | Routine | 0.005 | U | 0.87 |  | 1.77 |  | 1.22 |  | 1.06 |  | 0.27 |  | 7.2 | 08/07/2026
VP-260721 | 07/21/2026 | 06:30 | Routine | 0.005 | U | 1.21 |  | 4.09 |  | 1.57 |  | 1.27 |  | 0.35 |  | 8.4 | 07/30/2026
VP-260811 | 08/11/2026 | 06:45 | Routine | 0.014 |  | 0.66 |  | 4.33 |  | 2.61 |  | 0.89 |  | 0.19 |  | 6.8 | 08/20/2026
VP-260825 | 08/25/2026 | 06:50 | Routine | 0.005 | U | 0.74 |  | 4.15 |  | 1.9 |  | 1.18 |  | 0.29 |  | 7.5 | 09/04/2026
VP-260909 | 09/09/2026 | 06:40 | Routine | 0.012 |  | 1.02 |  | 2.96 |  | 1.36 |  | 3.14 |  | 0.41 |  | 7.9 | 09/15/2026
VP-260922 | 09/22/2026 | 06:35 | Routine | 0.005 | U | 0.58 |  | 1.68 |  | 0.98 |  | 0.94 |  | 0.24 |  | 7.3 | 10/01/2026
VP-260923 | 09/23/2026 | 07:05 | Resample | 0.005 | U | 0.49 |  | 1.52 |  | 1.11 |  | 0.88 |  |  | NS | 7.4 | 10/01/2026
A U result is reported at the MDL. Metals by EPA 200.7 on 24-hour flow-proportional composites; cyanide by SM 4500-CN E on grabs; field pH by the client's calibrated meter at collection.

## Sample Log
Chain of custody and analysis log
SAMPLE ID | COLLECTED | RECEIVED BY LAB | METALS ANALYZED | CYANIDE ANALYZED | CN HOLD DAYS | LAB NOTE
VP-260407 | 04/07/2026 06:40 | 04/08/2026 | 04/11/2026 | 04/12/2026 | 5
VP-260421 | 04/21/2026 06:35 | 04/22/2026 | 04/25/2026 | 04/23/2026 | 2
VP-260505 | 05/05/2026 06:50 | 05/06/2026 | 05/08/2026 | 05/10/2026 | 5
VP-260519 | 05/19/2026 06:45 | 05/20/2026 | 05/26/2026 | 05/25/2026 | 6 | Cyanide detected below the reporting limit; result qualified J
VP-260602 | 06/02/2026 06:40 | 06/03/2026 | 06/08/2026 | 06/07/2026 | 5
VP-260616 | 06/16/2026 06:55 | 06/17/2026 | 07/13/2026 | 06/18/2026 | 2 | Metals run held for the ICP-OES torch repair; digested 06/19, analyzed 07/13
VP-260707 | 07/07/2026 06:40 | 07/08/2026 | 08/06/2026 | 07/13/2026 | 6 | Metals digestate lost on the 07/12 run; re-digested from the retained aliquot and analyzed 08/06; report GLA-26-1611 issued 08/07 with the cyanide
VP-260721 | 07/21/2026 06:30 | 07/22/2026 | 07/26/2026 | 07/25/2026 | 4
VP-260811 | 08/11/2026 06:45 | 08/12/2026 | 08/15/2026 | 08/14/2026 | 3
VP-260825 | 08/25/2026 06:50 | 08/26/2026 | 09/28/2026 (Ni); 08/29/2026 (others) | 08/27/2026 | 2 | Nickel digestate lost in the instrument fault of 08/29; re-digested from the retained aliquot and nickel analyzed 09/28
VP-260909 | 09/09/2026 06:40 | 09/10/2026 | 09/12/2026 | 09/22/2026 | 13 | Cyanide distillation repeated 09/22 after the 09/12 spike recovery failed
VP-260922 | 09/22/2026 06:35 | 09/23/2026 | 09/30/2026 | 09/28/2026 | 6
VP-260923 | 09/23/2026 07:05 | 09/24/2026 | 09/26/2026 | not collected |  | Resample requested by client after the 09/09 event; cyanide grab not collected, metals only
Holding periods under 40 CFR Part 136 as the laboratory tracks them: 28 days from collection for total metals (preserved), 14 days for total cyanide (preserved); field pH at collection.

## Methods
Methods, detection limits and reporting limits
PARAMETER | METHOD | MDL MG/L | RL MG/L | SAMPLE TYPE
Cadmium, total | EPA 200.7 | 0.005 | 0.01 | 24-hour composite
Chromium, total | EPA 200.7 | 0.01 | 0.02 | 24-hour composite
Copper, total | EPA 200.7 | 0.01 | 0.02 | 24-hour composite
Nickel, total | EPA 200.7 | 0.02 | 0.04 | 24-hour composite
Zinc, total | EPA 200.7 | 0.02 | 0.04 | 24-hour composite
Cyanide, total | SM 4500-CN E | 0.005 | 0.01 | Grab
pH | SM 4500-H+ B, field | n/a | n/a | Grab at collection